## Heat Loss
ThermaXX LLC Heat Loss Analysis
Job Name | Sample job |  |  |  | REPORT SUMMARY: | [6 empty] | Therms Saved |  | Total Cost |  | Therms | CCF | MCF
Opp Number | 14346 |  |  |  | YEARLY SAVINGS IF INSULATED: |  |  |  |  | 16312.8524 |  | Jackets | 20391.0656 | 29469.5766 |  | 20391.0656 | 19777.9491 | 1977.7949 | Up to:
Date | 2018-12-12 |  |  |  | Total Insulation Jacket Cost: |  |  |  |  | 29469.5766 | [5 empty] | National Grid - NY | 1.5 | Per Therm | 50%
Cost/MMBTU | 8 |  |  |  | Incentive (if Applicable): |  |  |  |  | 14734.7883 |  | CO2 Greenhouse Reduction (MTons/yr)* |  |  | 109.1223 | Potential Incentive |  |  | 14734.7883
[5 empty] | Initial Payback in Months: |  |  |  |  | 10.8392 |  | *CO2 reduction of 118 pounds (0.059 Tons) for every MMBtu of natural gas saved.
Item | Location 1 | Location 2 | Location 3 | Description | Nominal Pipe Size | Pipe Straight Feet | Operating Temp ⁰F | Ambient Temp | SF/ component | Hrs in service/yr. | Insulation Thickness | Bare BTU/hr/sf lost | Insulated BTU/hr/sf lost | Insulated Touch Temp ⁰F | Dollars LOST per yr. if Uninsulated | Total Price | Payback in Months | Total yearly savings if insulated | Boiler Efficiency | Pre Therms | Post Therms | Therms Saved Per Year
32 | Heating plant | Piping for front of boiler 1 & 2 | - | 1" Hard Pipe Insulation x1' 1 1/2" | 1 | 33 | 338 | 90 | 13.78 | 8760 | 1.5" | 802.6 | 27.07 | 106 | 968.8409 | 710.9347 | 9.113 | 936.164 | 80% | 1211.0512 | 40.8462 | 1170.205
14 | Heating plant | Opposite # 13 | Other side of blue boiler | 1.25 PRV NPT (0-299°F) 1" | 1.25 | - | 259 | 90 | 0.71 | 8760 | 1" | 464.9 | 35.23 | 110 | 28.9149 | 290.4551 | 130.4256 | 26.7238 | 80% | 36.1437 | 2.739 | 33.4047
37 | Heating plant | Cross over Room | Against back walll | 1.25 PRV NPT (300-425°) - 1.5" | 1.25 | - | 353 | 90 | 0.71 | 8760 | 1.5" | 855.1 | 29.18 | 107 | 53.1838 | 317.2373 | 74.108 | 51.3689 | 80% | 66.4797 | 2.2686 | 64.2112
25 | Heating plant | Bottom front of boiler 1 | - | 1.5 Control Valve 250/300 1"+5mm (0°-299°F) | 1.5 | - | 353 | 90 | 2.58 | 8760 | 1"+5mm | 846 | 38.68 | 112 | 191.2028 | 437.7569 | 28.7902 | 182.4608 | 80% | 239.0035 | 10.9275 | 228.076
28 | Heating plant | Bottom front of boiler 2 | - | 1.5 Control Valve 250/300 1"+5mm (0°-299°F) | 1.5 | - | 353 | 90 | 2.58 | 8760 | 1"+5mm | 846 | 38.68 | 112 | 191.2028 | 437.7569 | 28.7902 | 182.4608 | 80% | 239.0035 | 10.9275 | 228.076
30 | Heating plant | Piping for front of boiler 1 & 2 | - | 1.5" Hard Pipe Insulation x1' 1.5" | 1.5 | 48 | 338 | 90 | 28.08 | 8760 | 1.5" | 777.8 | 30.81 | 108 | 1913.2387 | 1462.1736 | 9.5491 | 1837.452 | 80% | 2391.5483 | 94.7334 | 2296.815
33 | Heating plant | Cross over Room | Back left | 10 Gate Valve 250/300 (300-449°F) 1"+5mm | 10 | - | 353 | 90 | 11.28 | 8760 | 1"+5mm | 773.4 | 51.68 | 119 | 764.2182 | 1464.8518 | 24.6486 | 713.1517 | 80% | 955.2727 | 63.8331 | 891.4397
21 | Heating plant | Steam header | Next to 20 | 2 Blind Flange 250/300 1"+5mm (300-449°F) | 2 | - | 338 | 90 | 1.36 | 8760 | 1"+5mm | 765.2 | 37.55 | 112 | 91.1629 | 510.0687 | 70.6064 | 86.6893 | 80% | 113.9536 | 5.5919 | 108.3616
22 | Heating plant | Steam header | Next to 20 | 2 Gate Valve NPT (300-449°F) 15mm | 2 | - | 338 | 90 | 1.8 | 8760 | 15mm | 765.2 | 46.42 | 115 | 120.6567 | 443.1133 | 46.9163 | 113.3372 | 80% | 150.8209 | 9.1494 | 141.6715
35 | Heating plant | Cross over Room | Against back walll | 2 Gate Valve NPT (300-449°F) 15mm | 2 | - | 353 | 90 | 1.8 | 8760 | 15mm | 832.5 | 49.57 | 117 | 131.2686 | 443.1133 | 43.0721 | 123.4524 | 80% | 164.0857 | 9.7702 | 154.3155
4 | Heating plant | Back of Boiler 1 | - | 2 Globe Valve NPT (0-299°F) 15mm | 2 | - | 338 | 90 | 1.8 | 8760 | 15mm | 765.2 | 46.42 | 115 | 120.6567 | 473.9128 | 50.1773 | 113.3372 | 80% | 150.8209 | 9.1494 | 141.6715
5 | Heating plant | Back of Boiler 1 | Below 4 | 2 Globe Valve NPT (0-299°F) 15mm | 2 | - | 338 | 90 | 1.8 | 8760 | 15mm | 765.2 | 46.42 | 115 | 120.6567 | 473.9128 | 50.1773 | 113.3372 | 80% | 150.8209 | 9.1494 | 141.6715
10 | Heating plant | Top of Boiler 2 | - | 2 Globe Valve NPT (0-299°F) 15mm | 2 | - | 338 | 90 | 1.8 | 8760 | 15mm | 765.2 | 46.42 | 115 | 120.6567 | 473.9128 | 50.1773 | 113.3372 | 80% | 150.8209 | 9.1494 | 141.6715
11 | Heating plant | Top of Boiler 2 | Below 10 | 2 Globe Valve NPT (0-299°F) 15mm | 2 | - | 338 | 90 | 1.8 | 8760 | 15mm | 765.2 | 46.42 | 115 | 120.6567 | 473.9128 | 50.1773 | 113.3372 | 80% | 150.8209 | 9.1494 | 141.6715
36 | Heating plant | Cross over Room | Against back walll | 2 Wye Strainer NPT (300-449°F) 15mm | 2 | - | 353 | 90 | 1.62 | 8760 | 15mm | 832.5 | 49.57 | 117 | 118.1417 | 554.2592 | 59.8621 | 111.1072 | 80% | 147.6772 | 8.7932 | 138.884
6 | Heating plant | Back of Boiler 1 | Below 4 | 2" Hard Pipe Insulation x1' 1 1/2" | 2 | 21 | 338 | 90 | 14.04 | 8760 | 1.5" | 765.2 | 31.63 | 109 | 941.1225 | 678.7961 | 9.0283 | 902.2207 | 80% | 1176.4032 | 48.6273 | 1127.7758
12 | Heating plant | Back of Boiler 2 | - | 2" Hard Pipe Insulation x1' 1 1/2" | 2 | 21 | 338 | 90 | 14.04 | 8760 | 1.5" | 765.2 | 31.63 | 109 | 941.1225 | 678.7961 | 9.0283 | 902.2207 | 80% | 1176.4032 | 48.6273 | 1127.7758
31 | Heating plant | Piping for front of boiler 1 & 2 | - | 2" Hard Pipe Insulation x1' 1 1/2" | 2 | 30 | 338 | 90 | 21.84 | 8760 | 1.5" | 765.2 | 31.63 | 109 | 1463.9684 | 1001.5209 | 8.5633 | 1403.4544 | 80% | 1829.9605 | 75.6425 | 1754.318
42 | Heating plant | Cross over Room | Front right | 2" Hard Pipe Insulation x1' 1 1/2" | 2 | 60 | 353 | 90 | 41.6 | 8760 | 1.5" | 832.5 | 33.93 | 110 | 3033.7632 | 1822.3933 | 7.5147 | 2910.1169 | 80% | 3792.204 | 154.5579 | 3637.6461
34 | Heating plant | Cross over Room | Back left | 2.5 Gate Valve 250/300 (300-449°F) 1"+5mm | 2.5 | - | 353 | 90 | 3.49 | 8760 | 1"+5mm | 822 | 41.65 | 114 | 251.3051 | 625.2318 | 31.4487 | 238.5717 | 80% | 314.1314 | 15.9168 | 298.2147
19 | Heating plant | Steam header | Next to glycol | 3 Blind Flange 250/300 1"+5mm (300-449°F) | 3 | - | 338 | 90 | 1.75 | 8760 | 1"+5mm | 746.4 | 41.08 | 113 | 114.4231 | 574.3458 | 63.7421 | 108.1256 | 80% | 143.0289 | 7.872 | 135.1569
15 | Heating plant | Above glycol line | - | 3 Control Valve 125/150 (0-299°F) 1" | 3 | - | 259 | 90 | 1.47 | 8760 | 1" | 439.5 | 35.72 | 111 | 56.5953 | 464.539 | 107.2105 | 51.9956 | 80% | 70.7441 | 5.7497 | 64.9944
13 | Heating plant | Next to boiler 1 | Right of Asset 1 | 3 PRV 125/150 (0-299°F) 1" | 3 | - | 259 | 90 | 2.05 | 8760 | 1" | 439.5 | 35.72 | 111 | 78.9254 | 484.6256 | 80.2019 | 72.5108 | 80% | 98.6568 | 8.0182 | 90.6385
16 | Heating plant | Left of boiler 2 | - | 4 Gate Valve 250/300 (300-449°F) 1"+5mm | 4 | - | 338 | 90 | 5.43 | 8760 | 1"+5mm | 736.3 | 41.6 | 114 | 350.2343 | 834.1325 | 30.2911 | 330.4466 | 80% | 437.7929 | 24.7347 | 413.0582
38 | Heating plant | Cross over Room | Top front | 4 Gate Valve 250/300 (300-449°F) 1"+5mm | 4 | - | 353 | 90 | 5.43 | 8760 | 1"+5mm | 801.5 | 44.58 | 115 | 381.2479 | 834.1325 | 27.8011 | 360.0426 | 80% | 476.5599 | 26.5066 | 450.0533
40 | Heating plant | Cross over Room | Top front | 4 Gate Valve 250/300 (300-449°F) 1"+5mm | 4 | - | 353 | 90 | 5.43 | 8760 | 1"+5mm | 801.5 | 44.58 | 115 | 381.2479 | 834.1325 | 27.8011 | 360.0426 | 80% | 476.5599 | 26.5066 | 450.0533
41 | Heating plant | Cross over Room | Front right | 4 Gate Valve 250/300 (300-449°F) 1"+5mm | 4 | - | 353 | 90 | 5.43 | 8760 | 1"+5mm | 801.5 | 44.58 | 115 | 381.2479 | 834.1325 | 27.8011 | 360.0426 | 80% | 476.5599 | 26.5066 | 450.0533
39 | Heating plant | Cross over Room | Top front | 6 Gate Valve 250/300 (300-449°F) 1"+5mm | 6 | - | 353 | 90 | 6.92 | 8760 | 1"+5mm | 787.5 | 49.71 | 118 | 477.3762 | 994.8253 | 26.6922 | 447.2424 | 80% | 596.7202 | 37.6673 | 559.053
1 | Heating plant | Top of Boiler 1 | - | 6 Globe Valve 250/300 (300-449°F) 1"+5mm | 6 | - | 350 | 90 | 6.92 | 8760 | 1"+5mm | 774.5 | 49.04 | 117 | 469.4957 | 1219.7953 | 33.2847 | 439.768 | 80% | 586.8696 | 37.1596 | 549.7101
7 | Heating plant | Top of Boiler 2 | - | 6 Globe Valve 250/300 (300-449°F) 1"+5mm | 6 | - | 350 | 90 | 6.92 | 8760 | 1"+5mm | 774.5 | 49.04 | 117 | 469.4957 | 1219.7953 | 33.2847 | 439.768 | 80% | 586.8696 | 37.1596 | 549.7101
20 | Heating plant | Steam header | Next to glycol | 8 Flange 250/300 (300-449°F) 1"+5mm | 8 | - | 338 | 90 | 2.79 | 8760 | 1"+5mm | 715.7 | 45.27 | 116 | 174.9199 | 589.076 | 43.1411 | 163.8558 | 80% | 218.6499 | 13.8302 | 204.8197
23 | Heating plant | Steam header | Left of 22 | 8 Flange 250/300 (300-449°F) 1"+5mm | 8 | - | 338 | 90 | 2.79 | 8760 | 1"+5mm | 715.7 | 45.27 | 116 | 174.9199 | 589.076 | 43.1411 | 163.8558 | 80% | 218.6499 | 13.8302 | 204.8197
2 | Heating plant | Top of Boiler 1 | - | 8 Globe Valve 250/300 (300-449°F) 1"+5mm | 8 | - | 350 | 90 | 8.2 | 8760 | 1"+5mm | 766.5 | 47.96 | 117 | 550.5923 | 1392.5401 | 32.3758 | 516.1417 | 80% | 688.2403 | 43.0633 | 645.1771
8 | Heating plant | Top of Boiler 2 | - | 8 Globe Valve 250/300 (300-449°F) 1"+5mm | 8 | - | 350 | 90 | 8.2 | 8760 | 1"+5mm | 766.5 | 47.96 | 117 | 550.5923 | 1392.5401 | 32.3758 | 516.1417 | 80% | 688.2403 | 43.0633 | 645.1771
3 | Heating plant | Back of Boiler 1 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
9 | Heating plant | Top of Boiler 2 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
17 | Heating plant | Bottom back of boiler 1 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
18 | Heating plant | Bottom back of boiler 2 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
24 | Heating plant | Bottom front of boiler 1 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
26 | Heating plant | Top front of boiler 1 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
27 | Heating plant | Bottom front of boiler 2 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
29 | Heating plant | Top front of boiler 2 | - | Boiler Drum | - | - | 338 | 90 | 1.59 | 8760 | 1"+5mm | 776.7 | 51.05 | 117 | 108.1819 | 429.7222 | 51.02 | 101.0714 | 80% | 135.2274 | 8.8881 | 126.3393
[16 empty] | 29469.5766 |  | 16312.8524 |  | 21453.3872 | 1062.3216 | 20391.0656

## Project Highlight
Project Highlights
Job Name | Sample job
Opp Number | 14346
Date | 2018-12-12
Total Project Cost | 29469.5766
Total Jacket Savings | 16312.8524
Total Steam Trap Failure Prevention | 0
Total Yearly Savings | 16312.8524
Incentive | 14734.7883
ROI2 | 10.8392 | Months
ROI2= Amount of Time for initial Project payback (Incentive if applicable + Payback)
Payback in Months | 21.6783
5 Years of Savings | 81564.2622
Monthly Cost of waiting | 1359.4044
CO2 Greenhouse Reduction (Metric Tons/yr) | 109.1223 | CO2 reduction of 118 pounds (0.059 Tons) for every MMBtu of natural gas saved.
Pre Therms | 21453.3872
Post Therms | 1062.3216
Therms Saved | 20391.0656

## Incentives (hidden)
ConEd | 2 | Per Therm | 50% | 40782.1311 | 14734.7883
National Grid - NY | 1.5 | Per Therm | 50% | 30586.5983 | 14734.7883
National Grid - MA | 1.5 | Per Therm | 50% | 30586.5983 | 14734.7883
National Grid - RI | 1.5 | Per Therm | 50% | 30586.5983 | 14734.7883
Eversource - CT | 4 | Per CCF | 60% | 0 | 79111.7965
Eversource - MA | 1.5 | Per Therm | 50% | 30586.5983 | 14734.7883
Avangrid | 3.5 | Per CCF | 40% | 69222.822 | 11787.8306
DC SEU | 12 | Per MCF | 40% | 23733.539 | 11787.8306

## Steam Usage (hidden)
Pipe Heating Only | 3650
Pipe Cooling Only | 1800
Pipe Heating/Cooling/Hot Water | 8760
Duct Heating Only | 3650
Duct Cooling Only | 1800
Duct Heating and Cooling | 5450

## PIPE (hidden)
[8 empty] | Total Savings: |  | 0 | 0 | #VALUE! | [6 empty] | #VALUE!
|  | Steam heating pipe insulation savings: | [11 empty] | Steel, Fiberglass:
Pipe use | Pipe use | Pipe size (in) | Insulation thickness (existing) | Insulation thickness (proposed) | Insulation material | Pipe length (ft) | (UA/L)base | (UA/L)ee | Heating hours | Therms saved | Post | Pre | d | 0 | 0.5 | 1 | 1.5 | 2
Steam | Steam | [10 empty] | #VALUE! | 0.75 | 0.78 | 0.2 | 0.12 | 0.1 | 0.08
Hot Water | [11 empty] | #VALUE! | 1 | 0.95 | 0.23 | 0.14 | 0.11 | 0.09
[12 empty] | #VALUE! | 1.25 | 1.18 | 0.28 | 0.17 | 0.13 | 0.11
Pipe size | [11 empty] | #VALUE! | 1.5 | 1.33 | 0.31 | 0.18 | 0.14 | 0.12
0.75 | [11 empty] | #VALUE! | 2 | 1.63 | 0.37 | 0.21 | 0.16 | 0.13
1 | [11 empty] | #VALUE! | 2.5 | 1.94 | 0.44 | 0.25 | 0.18 | 0.15
1.25 | [11 empty] | #VALUE! | 3 | 2.32 | 0.52 | 0.29 | 0.21 | 0.17
1.5 | [11 empty] | #VALUE! | 4 | 2.92 | 0.65 | 0.36 | 0.26 | 0.21
2 | [11 empty] | #VALUE! | 5 | 3.6 | 0.79 | 0.43 | 0.31 | 0.25
2.5 | [12 empty] | 6 | 4.25 | 0.93 | 0.51 | 0.35 | 0.29
3 | [12 empty] | 7 | 4.91 | 1.07 | 0.58 | 0.4 | 0.33
4 | [12 empty] | 8 | 5.57 | 1.21 | 0.65 | 0.45 | 0.36
5 | [12 empty] | 9 | 6.22 | 1.35 | 0.72 | 0.5 | 0.4
6 | [12 empty] | 10 | 6.88 | 1.48 | 0.8 | 0.55 | 0.44
7 | [12 empty] | 11 | 7.53 | 1.62 | 0.87 | 0.6 | 0.48
8 | [12 empty] | 12 | 8.19 | 1.76 | 0.94 | 0.65 | 0.52
9 | [12 empty] | 13 | 8.84 | 1.9 | 1.02 | 0.69 | 0.56
10 | [12 empty] | 14 | 9.5 | 2.04 | 1.09 | 0.74 | 0.6
11
12
13
14
Insul thck
0
0.5
1
1.5
2
In mat
Fiberglass
Rigid foam

## Steam Trap Losses (hidden)
Steam System Assumptions |  |  | Sample job
Failed Traps Losses at 50% Total Steam Capacity
Leaking Traps Losses at 12.5% Total Steam Capacity
Cost of Fuel: |  | 8 | /MMBtu
Fuel Purchased |  | 100000 | MMBtu
Boiler Efficiency |  | 80%
Steam Produced |  | 80000 | Mlb
Cost of Steam: |  | 10 | /Mlb
[8 empty] | Single | Single | Total | Annual | Annual | Annual
| Steam |  | Steam | Orifice |  | 15% | 15% | Trap | Trap | Steam | Steam | Boiler | Economic
Hours/ | Press. |  | Trap | Dia. | Trap | Failed | Leaking | Failed | Leaking | Loss | Losses | Impact | Losses
Year | Psig | Equip. | Model | (Inches) | Qty | Qty | Qty | Loss/hr | Loss/hr | Lb/hr | Mlb/year | MMBtu/yr | $/year
8760 | 30 | Drip | BKT | 0.125 |  | 0 | 0 | 14.1084 | 3.5271 | 0 | 0 | 0 | 0
|  |  | TOTALS - |  | 0 | 0 | 0 |  |  |  | 0 |  | 0
[10 empty] | Steam Produced | 80000
[10 empty] | Boiler Savings | 0%
[10 empty] | CO2 Greenhouse Reduction (Tons/yr)* | 0
*CO2 reduction of 118 pounds (0.059 Tons) for every MMBtu of natural gas saved.

## Smart Jacket ROI (hidden)
Scope, Cost and Inputs
jackets | 400 | steam trap insulation jacket, 24" inlet insulation sleeve & 24" outlet insulation sleeve
Sensors | 400
Monitoring | 449
Total | 1249
Number of Sensors
| 0 | 0 | 0
| Sensors | Jacket Cost | Monitoring-3yrs | Project Total
| 0 | 0 | 0 | 0
|  | 10 | Sensors per Gateway | 0
|  |  | Project Cost | 0
Jacket Energy Savings per Year |  | 936.164
Labor for Trap Testing per Year |  | 120 | 2 hours at 60.00 per hour/trap/year
Blow thru & leaking trap Prevention |  | #DIV/0! | From steam trap losses tab
Plugged Trap |  | 0 | Nominal cost of $0.00/Trap
ROI
Qty | 0 | 0 | 0 | 0
Type | Jacket Savings | Inspection Labor | Trap Failure Prevention | Plugged Traps
2013 | 0 | 0 | #DIV/0! | 0
2014 | 0 | 0 | #DIV/0! | 0
2015 | 0 | 0 | #DIV/0! | 0
| 0 | 0 | #DIV/0! | 0
| Savings | #DIV/0!
| Yearly | #DIV/0!
|  | #DIV/0! | ROI Months + Plugged Trap Notification
CO2 Greenhouse Reduction (Tons/yr)* from blowing and leaking steam traps |  |  |  | 0
CO2 Greenhouse Reduction (Tons/yr)* from insulation jacket energy savings |  |  |  | 109.1223
Total CO2 Greenhouse Reduction (Tons/yr)* This project |  |  |  | 109.1223