SECTION XXX

REMOVABLE INSULATION JACKETS for STEAM

WARRANTY

Warranty all materials and labor for a period of Five Years

QUALITY ASSURANCE

Manufacturer Qualifications:  Company specializing in manufacturing the products specified in this Section with minimum Five years of documented experience.

Made in USA

PREFORMED THERMAL JACKETS

Manufacturers:

ThermaXX LLC 16 Hamilton Street West Haven CT 06516.

Insulation

For Box Type Jackets:

        - High-temperature insulation blanket formed of silica Aerogel and reinforced with a non-woven, glass-fiber batting.

        - Insulation must be hydrophobic

        - Estimation of Maximum Use Temperature 1200°F (650°C)

For Non Box Type Jackets:

        - Glass mat, type E needled fiber. ¼”, ½" @ 9 LB/CF & 1" @ 11.3 LB/CF. Maximum Use Temperature 1200°F (650°C)

        - Fiberglass mat with no chemical binders, type HP5 needled fiber. 1" @ 5 LB/CF. Maximum Use Temperature 1000°F (538°C)

All insulation materials shall be Non-Asbestos

Jacket Dry Location:

Hot Side

        - Silicone Fiberglass Composite Jacketing, 17 oz/sq. yd. minimum

        - Estimation of Maximum Use Temperature 450°F (232°C)

Cold Side

        - Silicone Fiberglass Composite Jacketing, 17 oz/sq. yd. minimum

        - Estimation of Maximum Use Temperature 450°F (232°C)

Jacket Wet Location (Steam Vaults/Pits):

Hot Side

        - All PTFE (Pure Teflon)- LFP 2110 13.5 oz/sq. yd. minimum

        - Estimation of Maximum Use Temperature 600°F (315°C)

Cold Side

        - All PTFE (Pure Teflon)- LFP 2110 13.5 oz/sq. yd. minimum

        - Estimation of Maximum Use Temperature 600°F (315°C)

Thread:

Kevlar

Begins to decompose at about 800 degrees (426 degrees C).

Does not melt

Diameter- .0114 inches

Break Point – 35LBS

Construction:

Sewn with lock stitch at a minimum of 4 to 6 stitches per inch.  Jackets shall be sewn using specified thread in section 1.3D. The thread must be able to withstand the skin temperatures without degradation.

Hog rings, staples and wire are not an acceptable methods of closure.

No raw cut jacket edges shall be exposed after install.

Jackets shall be fastened using hook and loop (Velcro) straps and D-rings.

Provide a permanently attached Laser Etched Anodized Aluminum nameplate (2” x 3.5”) on each jacket to identify its location and item number. Each nameplate must have a Laser Etched QR code linking to a website that contains the following information about that particular jacket:

        - Item Number

        - Location Information

        - Application Type

        - Operating Pressure

        - Component Type

        - Component Size

        - Jacket Min Max Temp

        - Insulation Thickness

        - Jacket material Hot Side

        - Jacket material Cold Side

        - Pre Photo & Post Photos

        - Pattern

An iPod or IOS App must be submitted, and training provided, upon project completion to display the website and items listed in section 5 above.

The insulation shall be designed to minimize the convection current in the space between the hot metal surface and the inner layer of insulation.

All jacket pieces which match mating seams must include an extended 2" flap constructed from the exterior fabric (or equivalent) and shall be secured using hook & loop closure (i.e. Velcro®) parallel to the seam.

Insulation must be sewn as integral part of the jacket to prevent shifting of the insulation. Insulation pins are NOT an allowable method of preventing the insulation from shifting and shall NOT be used.

Steam Trap Jackets must be constructed in a box shape for removal and replacement inspection ease.

COMPONENTS TO BE JACKETED INCLUDING BUT NOT LIMITED TO:

GATE, GLOBE and CHECK VALVE Type and Insulation Thickness Schedule

        - Crane

        - Nibco

        - Velan

        - Hammond

        - Stockham

        - Sharpe

        - Powell

WYE STRAINERs to be Jacketed

        - Keckley

        - Hoffman

        - Mueller

        - Nibco

        - Sarco

        - Powell

STEAM TRAPs to be Jacketed-Box Type Jacket

Inverted Bucket

        - Armstrong

Series 800-813

Series 814

Series 880

        - Spirax Sarco

Series B

Series 200

        - Hoffman

Series B0, B1, B2, B3, and B4

Float and Thermostatic-Box Type Jacket

        - Armstrong

Series A&B

        - Spirax Sarco

Series FT

        - Hoffman

Series H&I

PRV Types and Insulation Thickness Schedule

        - Armstrong

Series 2000

        - Spence

Series E

        - Sarco

Series P

        - Hoffman

Series 2000

        - Leslie

Series G

Control Valves

        - Fisher

        - VOGT

        - Limitorque

        - Watts

        - Johnson Controls

        - Belimo

Other Flanges, Unions, ETC

        - As required

JACKET PERFORMANCE & INSULATION THICKNESS

Insulation thickness: As required for Touch Temperature

Exterior of all jacket < 120F

END OF SECTION